## Summary all EPM prodcuts
SIL summary of Emerson Process Management ; revision 2 per 14 November 2003 | [17 empty] | made up by Aart Pruysen
Measuring equipment with 4-20 mA output | [17 empty] | Emerson Process Management - Europe
Logic solver detects hardware fault of measuring equipment when current outside the normal operating range (lower and upper current)
Trip does not occur with the lower and upper current (all detected failures result in dangerous detected failures)
|  |  | safe detected | safe undetected (no effect + unnunciation undetected) | dangerous detected | dangerous undetected | (λd = λdd + λdu) | (λs = λsd + λsu) | Safe Failure Fraction (calc. from dd; du; sd; su) | % Safe Failures | Diagnostic coverage dangerous(calc. from dd and du) | Diagnostic coverage safe (calc from sd and su) | PFD-average ; prooftestinterval one year | PFD lies within the range of |  |  |  | for internal purpose only
Typ | Product | Report | λ sd | λ su | λ dd | λ du | λ d | λ s | SFF | % S F | DCd | DCs | PFD | SIL Cap | MTBF | Risk reduction |  | fail high | fail detected | fail low inh. | dangerous undetected | no effect | annunciation undetected | with sensor; detectable | with sensor; undetectable
Rosemount Pressure | 3051C | FM/TUV Nov. 2000 | 0 | 19.57 | 556.65 | 145.65 | 702.3 | 19.57 | 79.82% | 2.711% | 79.26% | 0% | 0.00063795 | SIL 3 | MTBF 163 years | 1567.5283 | 162.5449 | FM/TUV report states directly sd ; su ; dd and du | [7 empty] | 3051C
Rosemount Pressure | 3051T | Ros 01/12-01 R111; Dec 2001 | 0 | 213 | 330 | 116 | 446 | 213 | 82.4% | 32.32% | 73.99% | 0% | 0.00050808 | SIL 3 | MTBF 256 years | 1968.194 | 255.9535 | 44 | 258 | 28 | 116 | 200 | 13 |  |  | 3051T
Rosemount Pressure | 3051S Coplanar | Ros 01/12-03 R110; Dec 2001 | 0 | 221 | 283 | 101 | 384 | 221 | 83.31% | 36.53% | 73.7% | 0% | 0.00044238 | SIL 3 | MTBF 297 years | 2260.5 | 297.2793 | 55 | 28 | 200 | 101 | 192 | 29 |  |  | 3051S Coplanar
Rosemount Pressure | 3051S In-line | Ros 01/12-03 R110; Dec 2001 | 0 | 213 | 259 | 83 | 342 | 213 | 85.05% | 38.38% | 75.73% | 0% | 0.00036354 | SIL 3 | MTBF 334 years | 2750.7289 | 333.7873 | 55 | 28 | 176 | 83 | 199 | 14 |  |  | 3051S In-line
Rosemount Temperature | 644H T/C w/o element | ROS03/05-11 August 2003 | 0 | 110 | 323 | 72 | 395 | 110 | 85.74% | 21.78% | 81.77% | 0% | 0.00031536 | SIL 3 | MTBF 289 years | 3170.9792 | 289.0006 | 26 | 274 | 23 | 72 | 101 | 9 |  |  | 644H T/C w/o element
Rosemount Temperature | 644H T/C with low stress T/C | ROS03/05-11 August 2003 | 0 | 110 | 5073 | 322 | 5395 | 110 | 94.15% | 1.998% | 94.03% | 0% | 0.0014104 | SIL 2 | MTBF 21 years | 709.0388 | 21.1595 | 26 | 274 | 23 | 72 | 101 | 9 | 4750 | 250 | 644H T/C with low stress T/C
Rosemount Temperature | 644H T/C with high stress T/C | ROS03/05-11 August 2003 | 0 | 110 | 19323 | 1072 | 20395 | 110 | 94.77% | 0.5365% | 94.74% | 0% | 0.0046954 | SIL 2 | MTBF 6 years | 212.9762 | 5.5972 | 26 | 274 | 23 | 72 | 101 | 9 | 19000 | 1000 | 644H T/C with high stress T/C
Rosemount Temperature | 644H RTD w/o element | ROS03/05-11 August 2003 | 0 | 114 | 316 | 70 | 386 | 114 | 86% | 22.8% | 81.87% | 0% | 0.0003066 | SIL 3 | MTBF 296 years | 3261.5786 | 295.739 | 26 | 267 | 23 | 70 | 105 | 9 |  |  | 644H RTD w/o element
Rosemount Temperature | 644H R with low stress RTD | ROS03/05-11 August 2003 | 0 | 114 | 2296 | 90 | 2386 | 114 | 96.4% | 4.56% | 96.23% | 0% | 0.0003942 | SIL 3 | MTBF 48 years | 2536.7834 | 47.8438 | 26 | 267 | 23 | 70 | 105 | 9 | 1980 | 20 | 644H R with low stress RTD
Rosemount Temperature | 644H R with high stress RTD | ROS03/05-11 August 2003 | 0 | 114 | 8236 | 150 | 8386 | 114 | 98.24% | 1.341% | 98.21% | 0% | 0.000657 | SIL 3 | MTBF 14 years | 1522.07 | 13.6126 | 26 | 267 | 23 | 70 | 105 | 9 | 7920 | 80 | 644H R with high stress RTD
0
Rosemount Temperature | 3144P T/C w/o element | ROS01/06-01 August 2001 | 0 | 336.7 | 377.01 | 79.29 | 456.3 | 336.7 | 90% | 42.46% | 82.62% | 0% | 0.00034729 | SIL 3 | MTBF 250 years | 2879.4363 | 250.1759 | 32.85 | 30 | 314.16 | 79.29 | 327.9 | 8.8 |  |  | 3144P T/C w/o element
Rosemount Temperature | 3144P with low stress T/C | ROS01/06-01 August 2001 | 0 | 336.7 | 5127.01 | 329.29 | 5456.3 | 336.7 | 94.32% | 5.812% | 93.96% | 0% | 0.0014423 | SIL 2 | MTBF 21 years | 693.3417 | 20.9217 | 32.85 | 30 | 314.16 | 79.29 | 327.9 | 8.8 | 4750 | 250 | 3144P with low stress T/C
Rosemount Temperature | 3144P with high stress T/C | ROS01/06-01 August 2001 | 0 | 336.7 | 19377.01 | 1079.29 | 20456.3 | 336.7 | 94.81% | 1.619% | 94.72% | 0% | 0.0047273 | SIL 3 | MTBF 6 years | 211.5377 | 5.5804 | 32.85 | 30 | 314.16 | 79.29 | 327.9 | 8.8 | 19000 | 1000 | 3144P with high stress T/C
Rosemount Temperature | 3144P 2 wire RTD w/o element | ROS01/06-01 August 2001 | 0 | 345.7 | 363.01 | 74.29 | 437.3 | 345.7 | 90.51% | 44.15% | 83.01% | 0% | 0.00032539 | SIL 3 | MTBF 261 years | 3073.2333 | 261.0456 | 32.85 | 30 | 300.16 | 74.29 | 336.9 | 8.8 |  |  | 3144P 2 wire RTD w/o element
Rosemount Temperature | 3144P RTD with 2-wire; low stress ; close | ROS01/06-01 August 2001 | 0 | 345.7 | 1963.01 | 474.29 | 2437.3 | 345.7 | 82.96% | 12.42% | 80.54% | 0% | 0.0020774 | SIL 2 | MTBF 47 years | 481.3732 | 46.8368 | 32.85 | 30 | 300.16 | 74.29 | 336.9 | 8.8 | 1600 | 400 | 3144P RTD with 2-wire; low stress ; close
Rosemount Temperature | 3144P RTD with 2-wire; low stress; extended | ROS01/06-01 August 2001 | 0 | 345.7 | 1763.01 | 674.29 | 2437.3 | 345.7 | 75.77% | 12.42% | 72.33% | 0% | 0.0029534 | SIL 2 | MTBF 47 years | 338.5939 | 46.8368 | 32.85 | 30 | 300.16 | 74.29 | 336.9 | 8.8 | 1400 | 600 | 3144P RTD with 2-wire; low stress; extended
Rosemount Temperature | 3144P RTD with 2-wire; high stress ; close | ROS01/06-01 August 2001 | 0 | 345.7 | 6763.01 | 1674.29 | 8437.3 | 345.7 | 80.94% | 3.936% | 80.16% | 0% | 0.0073334 | SIL 2 | MTBF 14 years | 136.3626 | 13.5298 | 32.85 | 30 | 300.16 | 74.29 | 336.9 | 8.8 | 6400 | 1600 | 3144P RTD with 2-wire; high stress ; close
Rosemount Temperature | 3144P RTD with 2-wire; high stress; extended | ROS01/06-01 August 2001 | 0 | 345.7 | 5963.01 | 2474.29 | 8437.3 | 345.7 | 71.83% | 3.936% | 70.67% | 0% | 0.010837 | SIL 1 | MTBF 14 years | 92.2731 | 13.5298 | 32.85 | 30 | 300.16 | 74.29 | 336.9 | 8.8 | 5600 | 2400 | 3144P RTD with 2-wire; high stress; extended
Rosemount Temperature | 3144P 3 wire RTD w/o element | ROS01/06-01 August 2001 | 0 | 341.9 | 366.81 | 74.29 | 441.1 | 341.9 | 90.51% | 43.67% | 83.16% | 0% | 0.00032539 | SIL 3 | MTBF 259 years | 3073.2333 | 258.7968 | 32.85 | 30 | 303.96 | 74.29 | 333.1 | 8.8 |  |  | 3144P 3 wire RTD w/o element
Rosemount Temperature | 3144P RTD with 3-wire; low stress ; close | ROS01/06-01 August 2001 | 0 | 341.9 | 1966.81 | 474.29 | 2441.1 | 341.9 | 82.96% | 12.29% | 80.57% | 0% | 0.0020774 | SIL 2 | MTBF 47 years | 481.3732 | 46.7639 | 32.85 | 30 | 303.96 | 74.29 | 333.1 | 8.8 | 1600 | 400 | 3144P RTD with 3-wire; low stress ; close
Rosemount Temperature | 3144P RTD with 3-wire; low stress; extended | ROS01/06-01 August 2001 | 0 | 341.9 | 1766.81 | 674.29 | 2441.1 | 341.9 | 75.77% | 12.29% | 72.38% | 0% | 0.0029534 | SIL 2 | MTBF 47 years | 338.5939 | 46.7639 | 32.85 | 30 | 303.96 | 74.29 | 333.1 | 8.8 | 1400 | 600 | 3144P RTD with 3-wire; low stress; extended
Rosemount Temperature | 3144P RTD with 3-wire; high stress ; close | ROS01/06-01 August 2001 | 0 | 341.9 | 6766.81 | 1674.29 | 8441.1 | 341.9 | 80.94% | 3.893% | 80.17% | 0% | 0.0073334 | SIL 2 | MTBF 14 years | 136.3626 | 13.5237 | 32.85 | 30 | 303.96 | 74.29 | 333.1 | 8.8 | 6400 | 1600 | 3144P RTD with 3-wire; high stress ; close
Rosemount Temperature | 3144P RTD with 3-wire; high stress; extended | ROS01/06-01 August 2001 | 0 | 341.9 | 5966.81 | 2474.29 | 8441.1 | 341.9 | 71.83% | 3.893% | 70.69% | 0% | 0.010837 | SIL 1 | MTBF 14 years | 92.2731 | 13.5237 | 32.85 | 30 | 303.96 | 74.29 | 333.1 | 8.8 | 5600 | 2400 | 3144P RTD with 3-wire; high stress; extended
Rosemount Temperature | 3144P 4 wire RTD w/o element | ROS01/06-01 August 2001 | 0 | 323.9 | 384.81 | 74.29 | 459.1 | 323.9 | 90.51% | 41.37% | 83.82% | 0% | 0.00032539 | SIL 3 | MTBF 249 years | 3073.2333 | 248.6501 | 32.85 | 30 | 321.96 | 74.29 | 315.1 | 8.8 |  |  | 3144P 4 wire RTD w/o element
Rosemount Temperature | 3144P RTD with 4-wire; low stress ; close | ROS01/06-01 August 2001 | 0 | 323.9 | 2364.81 | 94.29 | 2459.1 | 323.9 | 96.61% | 11.64% | 96.17% | 0% | 0.00041299 | SIL 3 | MTBF 46 years | 2421.365 | 46.4216 | 32.85 | 30 | 321.96 | 74.29 | 315.1 | 8.8 | 1980 | 20 | 3144P RTD with 4-wire; low stress ; close
Rosemount Temperature | 3144P RTD with 4-wire; low stress; extended | ROS01/06-01 August 2001 | 0 | 323.9 | 2364.81 | 94.29 | 2459.1 | 323.9 | 96.61% | 11.64% | 96.17% | 0% | 0.00041299 | SIL 3 | MTBF 46 years | 2421.365 | 46.4216 | 32.85 | 30 | 321.96 | 74.29 | 315.1 | 8.8 | 1980 | 20 | 3144P RTD with 4-wire; low stress; extended
Rosemount Temperature | 3144P RTD with 4-wire; high stress ; close | ROS01/06-01 August 2001 | 0 | 323.9 | 8304.81 | 154.29 | 8459.1 | 323.9 | 98.24% | 3.688% | 98.18% | 0% | 0.00067579 | SIL 3 | MTBF 13 years | 1479.7492 | 13.495 | 32.85 | 30 | 321.96 | 74.29 | 315.1 | 8.8 | 7920 | 80 | 3144P RTD with 4-wire; high stress ; close
Rosemount Temperature | 3144P RTD with 4-wire; high stress; extended | ROS01/06-01 August 2001 | 0 | 323.9 | 8304.81 | 154.29 | 8459.1 | 323.9 | 98.24% | 3.688% | 98.18% | 0% | 0.00067579 | SIL 3 | MTBF 13 years | 1479.7492 | 13.495 | 32.85 | 30 | 321.96 | 74.29 | 315.1 | 8.8 | 7920 | 80 | 3144P RTD with 4-wire; high stress; extended
MicroMotion flow | MVD 1700 option A | R03/05-01 - May 20, 2003 | 0 | 472 | 1805 | 257 | 2062 | 472 | 89.86% | 18.63% | 87.54% | 0% | 0.00135 | SIL 2 | MTBF 55 years | 740.7407 | 55.3614 | 7 | 1712 | 86 | 257 | 458 | 14 |  |  | MVD 1700 option A
MicroMotion flow I.s. output | MVD 1700 option D | R03/05-01 - May 20, 2003 | 0 | 469 | 1795 | 260 | 2055 | 469 | 89.7% | 18.58% | 87.35% | 0% | 0.00135 | SIL 2 | MTBF 56 years | 740.7407 | 55.55 | 46 | 1697 | 52 | 260 | 455 | 14 |  |  | MVD 1700 option D
MicroMotion flow | MVD 2700 option A | R03/05-1 (2) - May 20, 2003 | 0 | 472 | 1805 | 257 | 2062 | 472 | 89.86% | 18.63% | 87.54% | 0% | 0.00135 | SIL 2 | MTBF 55 years | 740.7407 | 55.3614 | 7 | 1712 | 86 | 257 | 458 | 14 |  |  | MVD 2700 option A
MicroMotion flow I.s. output | MVD 2700 option D | R03/05-1 (2) - May 20, 2003 | 0 | 469 | 1795 | 260 | 2055 | 469 | 89.7% | 18.58% | 87.35% | 0% | 0.00135 | SIL 2 | MTBF 56 years | 740.7407 | 55.55 | 46 | 1697 | 52 | 260 | 455 | 14 |  |  | MVD 2700 option D
MicroMotion flow | MVD 2700 option B & C | R03/05-1 (2) - May 20, 2003 | 0 | 463 | 1770 | 269 | 2039 | 463 | 89.25% | 18.51% | 86.81% | 0% | 0.00135 | SIL 2 | MTBF 56 years | 740.7407 | 55.9859 | 13 | 1667 | 90 | 269 | 449 | 14 |  |  | MVD 2700 option B & C
Rosemount flow | Vortex 8800C | R 02/07-14 - September 16, 2002 | 0 | 344 | 427 | 296 | 723 | 344 | 72.26% | 32.24% | 59.06% | 0% | 1.29E-03 | SIL 2 | MTBF 158 years | 775.1938 | 157.8911 | 75 | 310 | 42 | 296 | 344 | 0 |  |  | Vortex 8800C
Rosemount Flow | 8732C Magmeter DC option | ROS 03/07-26 October 2003 | 0 | 287 | 572 | 318 | 890 | 287 | 72.98% | 24.38% | 64.27% | 0% | 0.00139 | SIL 2 | MTBF 128 years | 719.4245 | 128.2643 | 6 | 480 | 86 | 318 | 271 | 16 |  |  | 8732C Magmeter DC option
Rosemount Flow | 8732C Magmeter AC option | ROS 03/07-26 October 2003 | 0 | 274 | 588 | 328 | 916 | 274 | 72.44% | 23.03% | 64.19% | 0% | 0.00144 | SIL 2 | MTBF 125 years | 694.4444 | 124.6236 | 6 | 514 | 68 | 328 | 258 | 16 |  |  | 8732C Magmeter AC option
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on Y24: aartpru: took % values from 3-wire
Note on Y25: aartpru: took % values from 3-wire
Note on Y26: aartpru: took % values from 3-wire
Note on Y27: aartpru: took % values from 3-wire
Note on Z24: aartpru: took % values from 3-wire
Note on Z25: aartpru: took % values from 3-wire
Note on Z26: aartpru: took % values from 3-wire
Note on Z27: aartpru: took % values from 3-wire